Fire Detection       Electrical Maintenance & Testing       Gas Detection

Service Report

| Service Type | Fire Alarm Service |
| --- | --- |
| Client Name | Merchants Quay Car-Park |
| Information | Carried out quarterly service of fire alarm system. Tested operation of sounders, smoke detectors and BGUs |
| Date | 07-09-2023 |
| Travel Start Time | 08:00 |
| Travel End Time | 08:00 |
| On Site Time | 08:30 |
| On Site Finish Time | 09:45 |
| System Information |  |
| Site Name and Contact Details | Tim Apcoa |
| Panel(s) Make and Model | Ctec conventional |
| Detection Type, Make and Model | Series 65 |
| Routine Service and Maintenance Details |  |
| System category for the area serviced, type YES after correct category | L2/L4 |
| Batteries tested | No |
| Load Test Meter Used | No |
| Battery age checked | Yes |
| Panel Checks |  |
| All functions checked including reset, mute, silence, etc. | Yes |
| All indicators checked including fire, fault, etc. | Yes |
| Field |  |
| Percentage of detection devices tested | Q3 service completed |
| Sounders Checked | Yes |
| DB Meter Used | No |
| Ancillary Outputs | Yes |
| Visual inspection of area serviced for any structural change since last service | Yes |
| Site logbook updated on service completion | Yes |
| Is fire alarm system set up for remote monitoring | Yes |
| Additional Information |  |
| Any system disablements or any items requiring attention should be listed here | Monitoring signal received by monitoring company ok however reset signal not received sue to line fault displaying on key panel. Advised Tim of this issue and he confirmed he was aware of it and he would make contact with alarm company |
| Has any equipment been supplied or installed during this visit | No |
| System left in normal working condition | Yes |
| Engineer Name | Thomas |
| Customer Name | MH |

Eltech Electrical Services Ltd

Unit 5 Lee Park, Site Cast Industrial Estate, Pouladuff Rd, Cork, T12YP8N

Vat No.: 6437035J

Tel 021-4289802

Mob: 086-6075532

Email: info@eltech.ie

Web: www.eltech.ie