Fire Detection       Electrical Maintenance & Testing       Gas Detection

Service Report

| Service Type | Fire Alarm Service |
| --- | --- |
| Client Name | Zazzle |
| Information | Carried out Quarterly service of the fire alarm system. Tested the operation of smoke and heat detectors. Carried out Sounder test. Signal confirmed with Top Security. |
| Date | 03-06-2025 |
| Travel Start Time | 08:00 |
| Travel End Time | 08:00 |
| On Site Time | 14:00 |
| On Site Finish Time | 15:00 |
| System Information |  |
| Site Name and Contact Details | Zazzle |
| Panel(s) Make and Model | Morley |
| Detection Type, Make and Model | Smoke, Heat, Break Glass, Sounders |
| Routine Service and Maintenance Details |  |
| System category for the area serviced, type YES after correct category | L2/L3 |
| Batteries tested | Yes |
| Load Test Meter Used | Yes |
| Battery age checked | Yes |
| Panel Checks |  |
| All functions checked including reset, mute, silence, etc. | Yes |
| All indicators checked including fire, fault, etc. | Yes |
| Field |  |
| Percentage of detection devices tested | 25% |
| Sounders Checked | Yes |
| DB Meter Used | Yes |
| Ancillary Outputs | Yes |
| Visual inspection of area serviced for any structural change since last service | Yes |
| Site logbook updated on service completion | Yes |
| Is fire alarm system set up for remote monitoring | No |
| Additional Information |  |
| Any system disablements or any items requiring attention should be listed here | The 2x 7ah batteries in the panel are over 3 years old and should be replaced at the next service. |
| Has any equipment been supplied or installed during this visit | No |
| System left in normal working condition | Yes |
| Engineer Name | Evan Walsh |
| Customer Name | Kate |

Eltech Electrical Services Ltd

Unit 5 Lee Park, Site Cast Industrial Estate, Pouladuff Rd, Cork, T12YP8N

Vat No.: 6437035J

Tel 021-4289802

Mob: 086-6075532

Email: info@eltech.ie

Web: www.eltech.ie